## NODES
NODES
Comment
| Create / Update Configuration |  |  | Check Configuration |  |  | Integration Tool Info
| User |  |  | User |  |  | Template Document ID
| Environment |  |  | Environment |  |  | Template Document Version | 1.0.0
| Result |  |  | Result |  |  | Integration Tool Version | 1.0.0
| Date |  |  | Date
Node Information
Result | Process | Name | Connector | Type | Description | Address | Subaddress | Redundancy | Username | Password | Custom | Comment
| NO | 1823907_PLS4000_ATS00753 | ATLNZ-V305-Con01 | OPC-UA |  | opc.tcp://10.250.103.53:4863 |  | ATLNZ-V305-Con02¦1823907_PLS4000_ATS00763
| NO | 1823907_PLS4000_ATS00763 | ATLNZ-V305-Con02 | OPC-UA |  | opc.tcp://10.250.103.63:4863
Note on B3: Comment: Ignored Use to provide additional comments / information for the configuration of this sheet. This table does not apply to configuration.
Note on B7: User: Do not modify. This field will be filled automatically. Username of the person who executed the action.
Note on E7: User: Do not modify. This field will be filled automatically. Username of the person who executed the action.
Note on H7: Document ID: Do not modify This field will be filled automatically. Reference to Integration Tool Template document in Veeva.
Note on B8: Environment: Do not modify This field will be filled automatically. Environment where the action is executed. Options: - DEV - QUAL - PROD
Note on E8: Environment: Do not modify This field will be filled automatically. Environment where the action is executed. Options: - DEV - QUAL - PROD
Note on H8: Document ID: Do not modify. This field will be filled automatically. Version of Integration Tool Template document.
Note on B9: Result: Do not modify. This field will be filled automatically. Result status of the action. Options: - OK: Action was executed successfully. - NOK: One or more errors occurred during the execution of the action.
Note on E9: Result: Do not modify. This field will be filled automatically. Result status of the action. Options: - OK: Action was executed successfully. - NOK: One or more errors occurred during the execution of the action.
Note on H9: Integration Tool Version: Do not modify. This field will be filled automatically. Integration Tool version.
Note on B10: Date: Do not modify. This field will be filled automatically. Timestamp of the execution.
Note on E10: Date: Do not modify. This field will be filled automatically. Timestamp of the execution.
Note on A13: Result: Do not modify. This field will be filled automatically. Options: OK: if the process has gone well. NOK: if the process has failed. N/A: if the row has not been processed.
Note on B13: Process: Required Type of processing to be performed. Options: - YES: Will process and enable the node and its children. - DIS: Will disable the node and its children. - NO*: Will not process the node. Example: YES *If the value is anything other than 'YES', 'NO' or 'DIS', the node will not be processed.
Note on C13: Name: Required Object name. Example: S7-DBA-S-01
Note on D13: Connector: Required Connector name. Example: ATLNZ-PS_Steril-4128_AL10-SCADA-01
Note on E13: Type: Required Datasource type. Options: Time Series: - Allen-Bradley - MODBUS - OPC-DA - OPC-UA - S7 - TIA Alarms and Events: - ODBC - OPC-AE - OPC-UA
Note on F13: Description: Optional Object description. Example: Node to connect to equipment ABC123.
Note on G13: Address: Required Address of the datasource. Options: Time Series: - Allen-Bradley:The hostname or IP address of the PLC. - MODBUS: The hostname or IP address of the modbus device. - OPC-DA: The Program Identifier (ProgID). - OPC-UA: The Server discovery or endpoint URL. - S7: The hostname or IP address of the PLC. - TIA: The hostname or IP address of the PLC. Alarms and Events: - ODBC: A valid ODBC connection string or DSN. In case of specifying a DSN, indicate Username and Passowrd in the Custom field. - OPC-AE: The Program Identifier (ProgID). - OPC-UA: The Server discovery or endpoint URL.
Note on H13: Subaddress: Required* Additional addressing configuration. MODBUS: Unit Identifier or slaveID. Format: <UnitID> Example: 1 S7: Concatenate the rack to which the plc is connected and the slot number. Format: <Rack>¦<Slot> Example: 0¦2 *Only required for the type S7 and MODBUS, leave empty otherwise.
Note on I13: Redundancy: Optional Name of the redundant connector and redundant datasource. Specify redundancy in primary node only. Format: <redConnectorName> ¦ <redDatasourceName> Example: ATLNZ-Node ¦ OPCUA-Equipment-01_R
Note on J13: Username: Optional* Username of the connection. *Only availabe for types OPC-UA, OPC-AE, OPC-DA and ODBC
Note on K13: Password: Optional* Password of the connection. *Only availabe for types OPC-UA, OPC-AE, OPC-DA and ODBC
Note on L13: Custom: Optional This column is used to enter specific properties that do not appear in the previous columns. - If more than one property is specified, divide by "¦". - If the property exists in the IO item / Redundant Item / ISA95 item, property is set. - If the property does not exist in any type of item mentioned in the previous point, the property is added as a custom property in the Redundant item and in the ISA95 item. Format: <CustomPropertyName01>:<Value01> ¦ <CustomPropertyName02>:<Value02> Note: To insert a property of type table, or a custom table, use the following format in the value field (you can copy and paste format and change the values as needed): { "<Column1Name>": [ <ValueRow1Column1>, <ValueRow2Column1> ], "<Column2Name>": [ <ValueRow1Column2>, <ValueRow2Column2> ] } Example: DisplayAlias: 1234 ¦ physicalTagLocation:under PV pump ¦ ConversionOutput: { "Incoming": ["1", "0"], "Output": [ "true", "false"] }
Note on M13: Comment: Ignored Use to provide additional comments / information for every row. This column does not apply to configuration.

## TAGS
TAGS
Comment
| Create / Update Configuration |  |  | Check Configuration |  |  | Integration Tool Info
| User |  |  | User |  |  | Template Document ID
| Environment |  |  | Environment |  |  | Template Document Version | 1.0.0
| Result |  |  | Result |  |  | Integration Tool Version
| Date |  |  | Date
| ISA95 |  |  | MES
| Enterprise |  |  | MES Name (ISA 95 Level)
Site
Area
Process Cell
Unit
Equipment
Tag Information
Result | Process | Group | Name | Description | Connector | Datasource | Item ID | Decimals | Eng Unit | Datastore | GMPCritical | ISA95 Generation | MES Name (Tag) | Conversion | Custom | Comment
Note on B3: Comment: Ignored Use to provide additional comments / information for the configuration of this sheet. This table does not apply to configuration.
Note on B7: User: Do not modify. This field will be filled automatically. Username of the person who executed the action.
Note on E7: User: Do not modify. This field will be filled automatically. Username of the person who executed the action.
Note on H7: Document ID: Do not modify This field will be filled automatically. Reference to Integration Tool Template document in Veeva.
Note on B8: Environment: Do not modify This field will be filled automatically. Environment where the action is executed. Options: - DEV - QUAL - PROD
Note on E8: Environment: Do not modify This field will be filled automatically. Environment where the action is executed. Options: - DEV - QUAL - PROD
Note on H8: Document ID: Do not modify. This field will be filled automatically. Version of Integration Tool Template document.
Note on B9: Result: Do not modify. This field will be filled automatically. Result status of the action. Options: - OK: Action was executed successfully. - NOK: One or more errors occurred during the execution of the action.
Note on E9: Result: Do not modify. This field will be filled automatically. Result status of the action. Options: - OK: Action was executed successfully. - NOK: One or more errors occurred during the execution of the action.
Note on H9: Integration Tool Version: Do not modify. This field will be filled automatically. Integration Tool version.
Note on B10: Date: Do not modify. This field will be filled automatically. Timestamp of the execution.
Note on E10: Date: Do not modify. This field will be filled automatically. Timestamp of the execution.
Note on B14: Enterprise: Do not modify. This field will be filled automatically. Options: - Takeda Assets
Note on E14: MES Name (ISA 95 Level): Optional. The MES name for the last object at the ISA 95 level. If left empty, the MES Name will default to the name of the ISA 95 Level. Example: AD1201
Note on B15: Site: Required Site name. Example: ATLNZ
Note on B16: Area: Required Area name. Example: PS_Steril
Note on B17: Process Cell: Optional Process Cell name. Example: DispensingLine
Note on B18: Unit: Optional Unit name. Example: Dispensing(CP82)
Note on B19: Equipment: Optional Equipment name. Example: BL20
Note on A22: Result: Do not modify. This field will be filled automatically. Options: OK: if the process has gone well. NOK: if the process has failed. N/A: if the row has not been processed.
Note on B22: Process: Required Type of processing to be performed Options: - YES: Will process and enable the tag. - DIS: Will disable the tag. - NO*: Will not process the tag. Example: YES *If the value is anything other than 'YES', 'NO' or 'DIS', the node will not be processed.
Note on C22: Group: Required Control Module name. Example: Dfr
Note on D22: Name: Required Tag name. Example: Actual Speed
Note on E22: Description: Optional Tag description. Example: Current operational Production line speed.
Note on F22: Connector: Required Object name of the connector. Example: ATLNZ-AL10-Node01
Note on G22: Datasource: Required Object name of the Datasource. Example: Colonne_CAT_001_OPC-UA
Note on H22: Item ID: Required The unique item identifier which has been configured in the external system. Options*: Allen-Bradley: Logix tag address. Format: [program name:]<tag name>[array indexes][.structure member][array index]...][.bit] Example: MachineSpeed, SpeedProgram:MachineSpeed MODBUS*: Location of an item of data in a Modbus Device. Format: MB.<Item Type code>:<Reference> Item type codes can be: Coils / Discrete Output: Code: 0, Object type: Single Bit Discrete Input: Code: 1, Object type: Single Bit Input Registers: Code 3, Object type: 16-bit word Holding Registers / Output Registers: Code 4, Object type: 16-bit word Examples: MB.4:123, MB.1:102 OPC-DA: Specification of the Item-ID from the OPC Server. Format: <symbolic name>. Even though not compulsory, standard format is: <OPCServerName>.<DataFolder>.<TagName> Example: OPCServer.SpeedProgram.MachineSpeed OPC-UA: Specification of the symbolic address. Specify between quotes: Format: "ns=<Namespaceindex>;s=<symbolicName>" Example: "ns=2;s=MachineSpeed" S7*: Specifier which describes a particular address in a specific PLC memory area. Format: <operand area><num>.<type code><offset>[.bit][array count] Supported types and their codes are*: BOOL = DBX, BOOL, X, BYTE = DBB, B, BYTE, CHAR = C, CHAR, INT = I, INT, DINT = DI, DINT, WORD = DBW, W, WORD, DWORD = DBD, D, DWORD, REAL = REAL, STRING = STRING, S5TIME = STIME, ST, S5TIME, TIME = T, TIME, DATE = DATE, TOD = TOD, DT = DT Examples: DB3.DBD30, DB5.DBW13, DB6.DBX3.5 TIA: Specification of the symbolic address: Datablocks: PLC.Blocks.<SymbolicName> Tagtable: PLC.Tags.Table.<SymbolicName> Example: PLC.Blocks.MainOB.MotorSpeed *ItemID input format will not be checked by the Integration Tool. Consult the inmation documentation for more information on ItemID requirements and formats.
Note on I22: Decimals: Optional Decimal resolution of the tag value. If the column is left empty, it defaults to 0. Example: 2
Note on J22: Eng Unit: Optional Engineering Unit Example: m/s
Note on K22: Datastore: Optional Name of the Datastore set where the data will be stored. If historical tracking is not desired, the cell should be left empty. Example: ATLNZ-globallocal-GxP-TS
Note on L22: GMPCritical: Required Indicates whether the tag is GMP critical or not. Options: - YES - NO
Note on M22: ISA95 Generation: Required Indicates the creation or presence of the tag in the ISA-95 Equipment Model. Options: - YES: Check or generate tag in the ISA-95 Equipment Model. - NO: Does not process the tag in the ISA-95 Equipment Model.
Note on N22: MES Name (Tag): Optional The MES Name of the tag. If left empty, the MES Name will default to the name of the tag. Example: ProductionCount_Solids
Note on O22: Conversion: Optional Specifies the conversion endured on the input values. Options: - Rescaling: If conversion mode is 'Rescaling', indicate the Raw and Phyisical ranges by their initials, concatenating with "¦". Format: RRL:<RawRangeLow> ¦ RRH:<RawRangeHigh> ¦ PRL:<PhysicalRangeLow> ¦ PRH:<PhysicalRangeHigh> Example: RRL: 0 ¦ RRH:100 ¦ PRL:10 ¦ PRH:1500 - Discrete State: If conversion mode is 'Discrete State', list the conversion table. Concatenate using "¦". Format: <OriginalValue>:<MappedValue> ¦ <OriginalValue2>:<MappedValue2> ... Example: 0:Stopped ¦ 1:Running
Note on P22: Custom: Optional This column is used to enter specific properties that do not appear in the previous columns. - If more than one property is specified, divide by "¦". - If the property exists in the IO item / Redundant Item / ISA95 item, property is set. - If the property does not exist in any type of item mentioned in the previous point, the property is added as a custom property in the Redundant item and in the ISA95 item. Format: <CustomPropertyName01>:<Value01> ¦ <CustomPropertyName02>:<Value02> Note: To insert a property of type table, or a custom table, use the following format in the value field (you can copy and paste format and change the values as needed): { "<Column1Name>": [ <ValueRow1Column1>, <ValueRow2Column1> ], "<Column2Name>": [ <ValueRow1Column2>, <ValueRow2Column2> ] } Example: DisplayAlias: 1234 ¦ physicalTagLocation:under PV pump ¦ ConversionOutput: { "Incoming": ["1", "0"], "Output": [ "true", "false"] }
Note on Q22: Comment: Ignored. Use to provide additional comments / information for every row. This column does not apply to configuration.

## ALARMS & EVENTS - AL
ALARMS/EVENTS
Comment
| Create / Update Configuration |  |  | Check Configuration
| User | hxv0242 |  | User
| Environment | DEV |  | Environment
| Result | OK |  | Result
| Date | 28.JUN.2024 20:09:04 (UTC+02:00) |  | Date
| ISA95 |  |  | Integration Tool Info
| Enterprise | Takeda Assets |  | Template Document ID
| Site | ATLNZ |  | Template Document Version | 1.0.0
| Area | SYST |  | Integration Tool Version | 1.0.0
| Process Cell | PCON
| Unit | 4000_PLS
| Equipment | PLS__1823907
Configuration
General Properties
| Connector | ATLNZ-V305-Con01
| Datasource | 1823907_PLS4000_ATS00753
| Datastore | ATLNZ-globallocal-GxP-EV-1
| Type | Alarms
| Only List | NO
| Monitor | NO
Timestamp Format
Table Name
Filter Column
Column Mapping
| Source Column | Inmation Column | Regular Expression
| Common.Message | MsgID
| Common.Message | MsgDescription
| Common.Timestamp | TimestampUTC
| u_.2041.2782.9011.9012.d_ | EnabledState
| u_.2041.2782.2881.2915.9160.9161.d_ | ActiveStateID
| u_.2041.2782.2881.9093.9094.d_ | AckedStateID
| u_.2041.WinCCEventType.CLASSID.d_ | ClassID
| u_.2041.WinCCEventType.CLASSNAME.d_ | ClassName
| u_.2041.WinCCEventType.TYPEID.d_ | TypeID
| u_.2041.WinCCEventType.TYPENAME.d_ | TypeName
| u_.2041.2045.d_ | OSSource
| u_.2041.WinCCEventType.STATETEXT.d_ | StateText
| u_.2041.WinCCEventType.USER.d_ | User
| u_.2041.WinCCEventType.OS_HIDDEN.d_ | OSHidden
| u_.2041.WinCCEventType.COMMENT.d_ | Comment
| u_.2041.WinCCEventType.OS_EVENTID.d_ | OSEventID
| u_.2041.WinCCEventType.PRIORITY.d_ | MsgSeverity
Format Mapping
| Formatting | Inmation Column
| {EnabledState} {ActiveStateID} {AckedStateID} | MsgState
Value Mapping
| Inmation Column | Source Value | Inmation Value
| MsgState | true true false | COME
| MsgState | true true true | COME ACK
| MsgState | true false false | GONE
| MsgState | true false true | GONE ACK
Inmation Mapping
| Inmation Column | Path | Inmation Condition Column | Operand | Inmation Value
Filter
| Inmation Column | Operand | Condition Value
| ClassID | EQ | 8 | Alarm
| ClassID | EQ | 9 | Warnung
| ClassID | EQ | 87 | Toleranz
|  |  |  | AS Leittechnik-Meldungen | 88
|  |  |  | OS Leittechnik-Meldungen | 89
|  |  |  | Vorbeugende Wartung | 90
|  |  |  | Prozessmeldung Klasse | 91
|  |  |  | Betriebsmeldung Klasse | 92
|  |  |  | Bedienanforderung Klasse | 93
|  |  |  | Bedienmeldung Klasse | 94
|  |  |  | Status-Meldung | 95
| ClassID | EQ | 6 | System, quittierpflichtig
|  |  |  | System, nicht quittierpflichtig | 96
Alarms/Events List
| MsgID | GMPCritical | Comment
Note on B3: Comment: Ignored Use to provide additional comments / information for the configuration of this sheet. This table does not apply to configuration.
Note on B7: User: Do not modify. This field will be filled automatically. Username of the person who executed the action.
Note on E7: User: Do not modify. This field will be filled automaticaly. Username of the person who executed the action.
Note on B8: Environment: Do not modify This field will be filled automatically. Environment where the action is executed. Options: - DEV - QUAL - PROD
Note on E8: Environment: Do not modify This field will be filled automatically. Environment where the action is executed. Options: - DEV - QUAL - PROD
Note on B9: Result: Do not modify. This field will be filled automatically. Result status of the action. Options: - OK: Action was executed successfully. - NOK: One or more errors occurred during the execution of the action.
Note on E9: Result: Do not modify. This field will be filled automaticaly. Result status of the action. Options: - OK: Action was executed successfully. - NOK: One or more errors occurred during the execution of the action.
Note on B10: Date: Do not modify. This field will be filled automatically. Timestamp of the execution.
Note on E10: Date: Do not modify. This field will be filled automaticaly. Timestamp of the execution.
Note on B14: Enterprise: Do not modify. This field will be filled automatically. Options: - Takeda Assets
Note on E14: Document ID: Do not modify This field will be filled automatically. Reference to Integration Tool Template document in Veeva.
Note on B15: Site: Required Site name. Example: ATLNZ
Note on E15: Document ID: Do not modify. This field will be filled automatically. Version of Integration Tool Template document.
Note on B16: Area: Required Area name. Example: PS_Steril
Note on E16: Integration Tool Version: Do not modify. This field will be filled automatically. Integration Tool version.
Note on B17: Process Cell: Optional Process Cell name. Example: DispensingLine
Note on B18: Unit: Optional Unit name. Example: Dispensing(CP82)
Note on B19: Equipment: Optional Equipment name. Example: BL20
Note on A22: Configuration: Required In this section the Alarm/Event config will be defined. The execution order for processing each alarm/event is the following: Workflow: 1. Column Mapping 2. Format Mapping 3. Inmation Mapping 4. Value Mapping 5. Filter 6. Alarms/Events List
Note on B25: General Properties: Required Configuration of general properties.
Note on B26: Connector: Required Object name of the Connector. Only specify the primary Connector in case of redundancy. Example: ATLNZ-AL10-01
Note on B27: Datasource: Required Object name of the Datasource. Only specify the primary Datasource in case of redundancy. Example: OPCUA-Colonne-CAT-01
Note on B28: Datastore: Required Name of the Datastore set where the data will be stored. Example: DEORA-local-GxP-EV-1
Note on B29: Type: Required Type of configuration. Options: - Alarms: Configuration for managing alarms. - Events: Configuration for managing system events and audit trail.
Note on B30: Only List: Required Indicates wheather only the alarms/events listed in the table Alarm/Event List will be processed. Options: - YES: Only alarms/events listed in the table will be processed. - NO: All alarms will be processed. The table will also be processed if it is not empty.
Note on B31: Monitor: Required. Indicate wheather a monitoring of the communication status of the Datasource will be performed. If 'YES' generate an alarm when the communcation is lost/restored Options: - YES: In case of loss of communication or restorage of connection, an alarm will be generated. The generated alarm will include the fields: - TimestampLocal: <Local timestamp of disconnection/reconnection>. - TimestampUTC: <UTC timestamp of disconnection/reconnection>. - MsgState: (one of) COME --> communication has been lost. GONE --> communication was lost but has been restored. - GMPCritical: YES. - MsgID: <Name of the Datasource>. - MsgDescription: Communication Lost. - NO: In case of loss of communication or reconnection, no alarm will be generated.
Note on B32: Timestamp Format: Optional Timestamp source format or formula to convert to POSIX time. Leave empty if timestamp format is already in POSIX. Example 1: 2020-06-19 = %Y-%m-%d Example 2: 10 Jun 2020 9:30:51 AM = %d %m %Y %H%M:%S Example 3: 09-02-2019 12:21:16 = %d-%m-%Y %H:%M:%S Example 4: 2024-05-04 03:23:43 = %Y-%m-%d %H:%M:%S Formula to convert to POSIX time. Indicate with "TIMESTAMP" the source value to convert from. Example 1: For Siemens HMI ({TIMESTAMP}/1000000) - 25569) * 86400 * 1000 Example 2: For Excel Spreadsheet = ({TIMESTAMP} - 25569) * 86400 * 1000
Note on B33: Table Name: Required* Name of the SQL table. Example: LYOEvents *Only specify for datasources of type ODBC.
Note on B34: Filter Column: Required* *Only specify for datasources of type ODBC. Column that will determine the filter of the query to retrieve data from the Database. Indicate the name of the Inmation Column and map it in the Column Mapping table. Options: - ID: Filter by higher auto-incremental row index. - TimestampUTC or TimestampLocal: Fliter by higher timestamp. As recommendation, use ID when possible. When filtering by Timestamp data loss can occur. Any alarm/event entered into the database with a timestamp earlier than the current one may be lost. If the Timestamp format is in string format the SQL data must be sorted. If the timestamp format is in string format, the alphabetical order of it must coincide with the chronological order of the data. If this is not fulfilled, the ID must be used as the Filter Column.
Note on B37: Column Mapping: Required Table to change the field names provided by the source to more generic or comprehensive names. Enhances comprehension in the system:inmation. Optionally, a regular expression can be applied to obtain a partial part or a segment of the source value. The regular expression is applied to the value of the Source Column. Workflow: 1. Map Source Column into an Inmation Column. 2. Apply Regular Expression to source values.
Note on B38: Source Column: Required Field names provided from the source. Example 1: For ODBC datasources, indicate the column names: Datetime, State, Name. Example 2: For OPC UA and OPC AE datasources, indicate the address of the fields recieved by the datasource in Inmation: u_.2041.WinCCEventType.PRIORITY.d_, for a Priority field; u_.2041.2047.d_, for a TimestampLocal; Common.Message, for the Message of the event.
Note on C38: Inmation Column: Required Name of the alarm/event field in the system:inmation. At the end of the configuration, the mapped Inmation Columns must adhere to the following criteria: Required Inmation Columns: - MsgID - MsgState (only required for Type 'Alarms'), (one of)*: - CAME - GONE - CAME ACK - GONE ACK - MsgDescription - TimestampUTC or TimestampLocal (only one is required, mapping both is optional) - ID (only required for ODBCs with Filter Column 'ID') Optional Inmation Columns: - GMPCritical (if not defined, this column will default to "NO"), (one of)*: - YES - NO - SfoID - OrderID - BatchID - ProductionUnit - EquipmentID - OperationID - PhaseID - StepID - User - UserComment Automatically mapped Inmation Columns: These columns are automatically mapped by the ITL and cannot be mapped. - EquipmentISA95 - MsgType - DatasourcePath Additional Information Exceptions that will be sent to MES: The exception will be mapped with the following priority: 1. SfoID 2. OrderID 3. BatchID 4. ProductionUnit 5. EquipmentID (if not mapped, it will be obtained from the MES Name of the ISA 95 Level. If the MES Name is empty, it will be obtained from the name of the object in the ISA-95 Equipment Model of SAIL) Custom Inmation Columns: In addition to the required and optional Inmation Columns, the system supports the definition of as many custom columns as needed. Custom columns will be historized as well. *The value needs to fit the standardized values.
Note on D38: Regular Expression: Optional Transformation of the source data. Indicate the Lua pattern to extract the data desired. Typically used to extract specific characters from a source. Example 1: Extract the event ID from an event log entry. Source Data: "EventID: 4567 - Alarm triggered at zone 3" Regular Expression: "EventID: (%d+)" --> Matches the digits following "EventID: ", capturing the event ID number. Returns: "4567" Example 2: Extract the timestamp from an alarm log entry. Source Data: "Alarm at 2024-05-29 14:32:21 - Zone 5" Regular Expression: "(%d%d%d%d%-%d%d%-%d%d %d%d:%d%d:%d%d)" --> Matches the timestamp in the format "YYYY-MM-DD HH:MM". Returns: "2024-05-29 14:32:21" Example 3: Extract the alarm type from an alarm log entry. Source Data: "AlarmType: Fire - Location: Warehouse" Regular Expression: "AlarmType: (%a+)" --> Matches the word following "AlarmType: ", capturing the type of alarm. Returns: "Fire"
Note on B58: Format Mapping: Optional Table to format Inmation Columns resultant form the Column Mapping or to create new ones. - Use "{}" to encapsulate/indicate an Inmation Column. - All other characters will be treated as fixed values. Workflow: Update the value of an Inmation Column with the formatting specified in the Formatting column. If the Inmation Column does not exists, create an Inmation Column with the value specified in the Formatting column. Note: the format in the examples is <Formatting>; <Inmation Column>. Example 1: {MsgID} {Name}; MsgDescription --> Creates/Updates the Inmation Column "MsgDescription" with the concatenation of the two columns. If MsgID = 122 and Name = "RPM high", then the resultant column: MsgDescription = "122 RPM high". Example 2: LOW; Severity --> Creates/Updates the Inmation Column "Severity" with the values: Severity = "LOW". Example 3: alarmID: {MsgID}; id2 --> Creates/Updates the Inmation Column "id2" with the fixed value "alarmID: ". The resultant column (note: same MsgID as the Example1): id2 = "alarmID: 122". Example 4: {description1} - {description2}; description3 --> Creates/Updates the Inmation Column "description3". If description1= "RPM too high" and descrption2="Over 4000", then the resultant column: descripiton3="RPM too high - Over 4000".
Note on B59: Formatting: Required Formatting endured to create/update a new/existing Inmation Column. Encapsulate the names of Inmation Columns in between brackets "{...}". All other characters will be treated as fixed values. Example 1: Concatenation of two columns: {Descripiton}{Severity} Example 2: Adding a new column with the fixed value LOW: LOW Example 3: Combination of a fixed value with a source column: alarmID: {ID} Example 4: Combination of two source columns with a fixed value in between: {description1} - {description2}
Note on C59: Inmation Column: Required Name of the alarm/event field in the system:inmation. At the end of the configuration, the mapped Inmation Columns must adhere to the following criteria: Required Inmation Columns: - MsgID - MsgState (only required for Type 'Alarms'), (one of)*: - CAME - GONE - CAME ACK - GONE ACK - MsgDescription - TimestampUTC or TimestampLocal (only one is required, mapping both is optional) - ID (only required for ODBCs with Filter Column 'ID') Optional Inmation Columns: - GMPCritical (if not defined, this column will default to "NO"), (one of)*: - YES - NO - SfoID - OrderID - BatchID - ProductionUnit - EquipmentID - OperationID - PhaseID - StepID - User - UserComment Automatically mapped Inmation Columns: These columns are automatically mapped by the ITL and cannot be mapped. - EquipmentISA95 - MsgType - DatasourcePath Additional Information Exceptions that will be sent to MES: The exception will be mapped with the following priority: 1. SfoID 2. OrderID 3. BatchID 4. ProductionUnit 5. EquipmentID (if not mapped, it will be obtained from the MES Name of the ISA 95 Level. If the MES Name is empty, it will be obtained from the name of the object in the ISA-95 Equipment Model of SAIL) Custom Inmation Columns: In addition to the required and optional Inmation Columns, the system supports the definition of as many custom columns as needed. Custom columns will be historized as well. *The value needs to fit the standardized values.
Note on B65: Value Mapping: Optional Table to map the values given by the source to more comprehensive or meaningful values. Workflow: If the Source Value matches the value of the Inmation Column, then overwrite the Inmation Column with the value specified in the Inmation Value. - The Source Value can be defined as "{Default}", which will set a default Inmation Value in case no condition is matched. - To specify a null value, type "{nil}". Note: the format in the examples is <Inmation Column>; <Source Value>; <Inmation Value>. Example 1: StateID; 1; CAME --> if the source value of the inmation field StateID is 1 then overwrite StateID with the value CAME. Example 2: Severity; 0; HIGH --> if the source value of the inmation field Severity is 0 then overwrite Severity with the value GONE.
Note on B66: Inmation Column: Required Name of the alarm/event field in the system:inmation. At the end of the configuration, the mapped Inmation Columns must adhere to the following criteria: Required Inmation Columns: - MsgID - MsgState (only required for Type 'Alarms'), (one of)*: - CAME - GONE - CAME ACK - GONE ACK - MsgDescription - TimestampUTC or TimestampLocal (only one is required, mapping both is optional) - ID (only required for ODBCs with Filter Column 'ID') Optional Inmation Columns: - GMPCritical (if not defined, this column will default to "NO"), (one of)*: - YES - NO - SfoID - OrderID - BatchID - ProductionUnit - EquipmentID - OperationID - PhaseID - StepID - User - UserComment Automatically mapped Inmation Columns: These columns are automatically mapped by the ITL and cannot be mapped. - EquipmentISA95 - MsgType - DatasourcePath Additional Information Exceptions that will be sent to MES: The exception will be mapped with the following priority: 1. SfoID 2. OrderID 3. BatchID 4. ProductionUnit 5. EquipmentID (if not mapped, it will be obtained from the MES Name of the ISA 95 Level. If the MES Name is empty, it will be obtained from the name of the object in the ISA-95 Equipment Model of SAIL) Custom Inmation Columns: In addition to the required and optional Inmation Columns, the system supports the definition of as many custom columns as needed. Custom columns will be historized as well. *The value needs to fit the standardized values.
Note on C66: Source Value: Required Source value to be compared against. The Source Value can be defined as "{Default}", which will set a default Inmation Value in case no condition is matched. To specify a null value, type "{nil}". Example: 0, {Default}, {nil}
Note on D66: Inmation Value: Required Value of the field after the mapping. Example: CAME
Note on B74: Inmation Mapping: Optional Map the Inmation Column with the value of a tag in the system:inmation if a condition is met. - The value of the inmation tag will be obtained from the path of the object indicated in the Path column. - The condition is composed by the columns Inmation Condition Column, Operand and Inmation Value, and has the form: <Inmation Condition Column> <Operand> <Inmation Value>. Condition: - Indicate a default case leaving the 3 condition columns empty. - If a default case, the Inmation Column will always be populated with the value of the inmation tag. - If a condition is specified, the value will be mapped only if the condition is true. - If a condition is specified but not met and no default case is specified, the Inmation Column will not be mapped. - Cases with a matching condition always take precedence over default cases, overwriting them. - If two or more matching conditions are defined, only the latter takes precedence. Note: The format in the examples is <Inmation Column>; <Path>; <Inmation Condition Column>; <Operand>; <Inmation Value>. Example 1: SfoID; <path>; BatchID; EQ; Room01 --> if the value of the BatchID field matches "Room01", then populate the column SfoID with the value of the inmation tag. Example 2: SfoID; <path>; (empty); (empty); (empty) --> Populate a new column called SfoID with the value of the inmation tag.
Note on B75: Inmation Column: Required Name of the alarm/event field in the system:inmation. At the end of the configuration, the mapped Inmation Columns must adhere to the following criteria: Required Inmation Columns: - MsgID - MsgState (only required for Type 'Alarms'), (one of)*: - CAME - GONE - CAME ACK - GONE ACK - MsgDescription - TimestampUTC or TimestampLocal (only one is required, mapping both is optional) - ID (only required for ODBCs with Filter Column 'ID') Optional Inmation Columns: - GMPCritical (if not defined, this column will default to "NO"), (one of)*: - YES - NO - SfoID - OrderID - BatchID - ProductionUnit - EquipmentID - OperationID - PhaseID - StepID - User - UserComment Automatically mapped Inmation Columns: These columns are automatically mapped by the ITL and cannot be mapped. - EquipmentISA95 - MsgType - DatasourcePath Additional Information Exceptions that will be sent to MES: The exception will be mapped with the following priority: 1. SfoID 2. OrderID 3. BatchID 4. ProductionUnit 5. EquipmentID (if not mapped, it will be obtained from the MES Name of the ISA 95 Level. If the MES Name is empty, it will be obtained from the name of the object in the ISA-95 Equipment Model of SAIL) Custom Inmation Columns: In addition to the required and optional Inmation Columns, the system supports the definition of as many custom columns as needed. Custom columns will be historized as well. *The value needs to fit the standardized values.
Note on C75: Path: Required Path of the tag in the system:inmation. Specify relative path of the redundant items folder, starting from the Site level: /<Site>/<Area>/ ... Example: /ATLNZ/Line C/BufferPreparation/BagDistribution(CB90)/D101/CB90_D101_VE_batch_ID
Note on D75: Inmation Condition Column: Optional Specify the Inmation Column whose value will be compared against the Inmation Value. To specify a default condition, leave the field empty. Examples: Datetime, State, Name, (empty).
Note on E75: Operand: Optional Operand of the boolean expression. To specify a default condition, leave the field empty. Options: - LT : Less than - GT : Greater than - LTE : Less or equal than - GTE : Greater or equal than - EQ : Equal to - NE : Not equal to - (empty) : Indicates default condition
Note on F75: Inmation Value: Optional Value that will be used to create the condition. It will be compared against the Inmation Condition Column. To specify a default condition, leave the field empty. To specify a null value, type "{nil}". Example: Room01, (empty).
Note on B81: Filter: Optional Table that defines which alarms/events pass the filter (will be processed). Workflow: If more than one filter is specified for the same Inmation Column, then the filters are concatenated with an OR operator. The concatenation between different Inmation Columns is done by an AND operator. Note: the format in the examples is <Inmation Column >; <Operand>; <Condition Value> Example 1: MsgState; EQ; CAME MsgState; EQ; GONE --> process those alarms which state value is CAME or GONE. Example 2: Priority; EQ; CRITICAL Severity; EQ; HIGH --> process those alarms with a priority CRITICAL and, of those, the ones that have a severity equal to HIGH.
Note on B82: Inmation Column: Required Name of the alarm/event field in the system:inmation. At the end of the configuration, the mapped Inmation Columns must adhere to the following criteria: Required Inmation Columns: - MsgID - MsgState (only required for Type 'Alarms'), (one of)*: - CAME - GONE - CAME ACK - GONE ACK - MsgDescription - TimestampUTC or TimestampLocal (only one is required, mapping both is optional) - ID (only required for ODBCs with Filter Column 'ID') Optional Inmation Columns: - GMPCritical (if not defined, this column will default to "NO"), (one of)*: - YES - NO - SfoID - OrderID - BatchID - ProductionUnit - EquipmentID - OperationID - PhaseID - StepID - User - UserComment Automatically mapped Inmation Columns: These columns are automatically mapped by the ITL and cannot be mapped. - EquipmentISA95 - MsgType - DatasourcePath Additional Information Exceptions that will be sent to MES: The exception will be mapped with the following priority: 1. SfoID 2. OrderID 3. BatchID 4. ProductionUnit 5. EquipmentID (if not mapped, it will be obtained from the MES Name of the ISA 95 Level. If the MES Name is empty, it will be obtained from the name of the object in the ISA-95 Equipment Model of SAIL) Custom Inmation Columns: In addition to the required and optional Inmation Columns, the system supports the definition of as many custom columns as needed. Custom columns will be historized as well. *The value needs to fit the standardized values.
Note on C82: Operand: Required Operand of the boolean expression. Options: - LT : Less than - GT : Greater than - LTE : Less or equal than - GTE : Greater or equal than - EQ : Equal to - NE : Not equal to
Note on D82: Condition Value: Required Value that will be processed in the boolean expression. Options: - Any string value : String value - Any numeric value : Numeric value - TRUE, FALSE : Boolean - {nil} : Null Examples: Alarm01, 100, CRITICAL, TRUE, {nil}
Note on B98: Alarms/Events List: Optional* This table indicates the list of relevant alarms/events. If Only List is set to 'YES', only the Alarms/Events specified here will be processed. - The column MsgID matches the MsgID of the Inmation Column defined in the configuration. - The column GMPCritical overwrites the resultant GMPCritical obtained. - The Comment column will be ignored when processing the Alarm/Event. Use it to provide a comment of the row. Workflow: The alarms/events specified here will be processed. The GMPCritical field of the Alarm/Event indicated by the MsgID will be updated. *If Only List is set to 'YES', this table is required.
Note on B99: MsgID: Required MsgID of the alarm/event Examples: 001, AL24-32
Note on C99: GMPCritical: Required Indicates if the alarm is GMPCritical or not. The GMPCritical indicated here overwrites the GMPCritical resultant of the configuration. Options: - YES - NO
Note on D99: Comment: Ignored Use to provide additional comments/information for the configuration of this alarm/event. This column will not be processed as an Inmation Column.

## ALARMS & EVENTS - EV
ALARMS/EVENTS
Comment
| Create / Update Configuration |  |  | Check Configuration
| User | hxv0242 |  | User
| Environment | DEV |  | Environment
| Result | OK |  | Result
| Date | 28.JUN.2024 20:08:57 (UTC+02:00) |  | Date
| ISA95 |  |  | Integration Tool Info
| Enterprise | Takeda Assets |  | Template Document ID
| Site | ATLNZ |  | Template Document Version | 1.0.0
| Area | SYST |  | Integration Tool Version | 1.0.0
| Process Cell | PCON
| Unit | 4000_PLS
| Equipment | PLS__1823907
Configuration
General Properties
| Connector | ATLNZ-V305-Con01
| Datasource | 1823907_PLS4000_ATS00753
| Datastore | ATLNZ-globallocal-GxP-EV-1
| Type | Events
| Only List | NO
| Monitor | NO
Timestamp Format
Table Name
Filter Column
Column Mapping
| Source Column | Inmation Column | Regular Expression
| Common.Message | MsgID
| Common.Message | MsgDescription
| Common.Timestamp | TimestampUTC
| u_.2041.2782.9011.9012.d_ | EnabledState
| u_.2041.2782.2881.2915.9160.9161.d_ | ActiveStateID
| u_.2041.2782.2881.9093.9094.d_ | AckedStateID
| u_.2041.WinCCEventType.CLASSID.d_ | ClassID
| u_.2041.WinCCEventType.CLASSNAME.d_ | ClassName
| u_.2041.WinCCEventType.TYPEID.d_ | TypeID
| u_.2041.WinCCEventType.TYPENAME.d_ | TypeName
| u_.2041.2045.d_ | OSSource
| u_.2041.WinCCEventType.STATETEXT.d_ | StateText
| u_.2041.WinCCEventType.USER.d_ | User
| u_.2041.WinCCEventType.OS_HIDDEN.d_ | OSHidden
| u_.2041.WinCCEventType.COMMENT.d_ | Comment
| u_.2041.WinCCEventType.OS_EVENTID.d_ | OSEventID
| u_.2041.WinCCEventType.PRIORITY.d_ | MsgSeverity
Format Mapping
| Formatting | Inmation Column
Value Mapping
| Inmation Column | Source Value | Inmation Value
Inmation Mapping
| Inmation Column | Path | Inmation Condition Column | Operand | Inmation Value
Filter
| Inmation Column | Operand | Condition Value
|  |  |  | Alarm | 8
|  |  |  | Warnung | 9
|  |  |  | Toleranz | 87
| ClassID | EQ | 88 | AS Leittechnik-Meldungen
| ClassID | EQ | 89 | OS Leittechnik-Meldungen
| ClassID | EQ | 90 | Vorbeugende Wartung
| ClassID | EQ | 91 | Prozessmeldung Klasse
| ClassID | EQ | 92 | Betriebsmeldung Klasse
| ClassID | EQ | 93 | Bedienanforderung Klasse
| ClassID | EQ | 94 | Bedienmeldung Klasse
| ClassID | EQ | 95 | Status-Meldung
|  |  |  | System, quittierpflichtig | 6
| ClassID | EQ | 96 | System, nicht quittierpflichtig
Alarms/Events List
| MsgID | GMPCritical | Comment
Note on B3: Comment: Ignored Use to provide additional comments / information for the configuration of this sheet. This table does not apply to configuration.
Note on B7: User: Do not modify. This field will be filled automatically. Username of the person who executed the action.
Note on E7: User: Do not modify. This field will be filled automaticaly. Username of the person who executed the action.
Note on B8: Environment: Do not modify This field will be filled automatically. Environment where the action is executed. Options: - DEV - QUAL - PROD
Note on E8: Environment: Do not modify This field will be filled automatically. Environment where the action is executed. Options: - DEV - QUAL - PROD
Note on B9: Result: Do not modify. This field will be filled automatically. Result status of the action. Options: - OK: Action was executed successfully. - NOK: One or more errors occurred during the execution of the action.
Note on E9: Result: Do not modify. This field will be filled automaticaly. Result status of the action. Options: - OK: Action was executed successfully. - NOK: One or more errors occurred during the execution of the action.
Note on B10: Date: Do not modify. This field will be filled automatically. Timestamp of the execution.
Note on E10: Date: Do not modify. This field will be filled automaticaly. Timestamp of the execution.
Note on B14: Enterprise: Do not modify. This field will be filled automatically. Options: - Takeda Assets
Note on E14: Document ID: Do not modify This field will be filled automatically. Reference to Integration Tool Template document in Veeva.
Note on B15: Site: Required Site name. Example: ATLNZ
Note on E15: Document ID: Do not modify. This field will be filled automatically. Version of Integration Tool Template document.
Note on B16: Area: Required Area name. Example: PS_Steril
Note on E16: Integration Tool Version: Do not modify. This field will be filled automatically. Integration Tool version.
Note on B17: Process Cell: Optional Process Cell name. Example: DispensingLine
Note on B18: Unit: Optional Unit name. Example: Dispensing(CP82)
Note on B19: Equipment: Optional Equipment name. Example: BL20
Note on A22: Configuration: Required In this section the Alarm/Event config will be defined. The execution order for processing each alarm/event is the following: Workflow: 1. Column Mapping 2. Format Mapping 3. Inmation Mapping 4. Value Mapping 5. Filter 6. Alarms/Events List
Note on B25: General Properties: Required Configuration of general properties.
Note on B26: Connector: Required Object name of the Connector. Only specify the primary Connector in case of redundancy. Example: ATLNZ-AL10-01
Note on B27: Datasource: Required Object name of the Datasource. Only specify the primary Datasource in case of redundancy. Example: OPCUA-Colonne-CAT-01
Note on B28: Datastore: Required Name of the Datastore set where the data will be stored. Example: DEORA-local-GxP-EV-1
Note on B29: Type: Required Type of configuration. Options: - Alarms: Configuration for managing alarms. - Events: Configuration for managing system events and audit trail.
Note on B30: Only List: Required Indicates wheather only the alarms/events listed in the table Alarm/Event List will be processed. Options: - YES: Only alarms/events listed in the table will be processed. - NO: All alarms will be processed. The table will also be processed if it is not empty.
Note on B31: Monitor: Required. Indicate wheather a monitoring of the communication status of the Datasource will be performed. If 'YES' generate an alarm when the communcation is lost/restored Options: - YES: In case of loss of communication or restorage of connection, an alarm will be generated. The generated alarm will include the fields: - TimestampLocal: <Local timestamp of disconnection/reconnection>. - TimestampUTC: <UTC timestamp of disconnection/reconnection>. - MsgState: (one of) COME --> communication has been lost. GONE --> communication was lost but has been restored. - GMPCritical: YES. - MsgID: <Name of the Datasource>. - MsgDescription: Communication Lost. - NO: In case of loss of communication or reconnection, no alarm will be generated.
Note on B32: Timestamp Format: Optional Timestamp source format or formula to convert to POSIX time. Leave empty if timestamp format is already in POSIX. Example 1: 2020-06-19 = %Y-%m-%d Example 2: 10 Jun 2020 9:30:51 AM = %d %m %Y %H%M:%S Example 3: 09-02-2019 12:21:16 = %d-%m-%Y %H:%M:%S Example 4: 2024-05-04 03:23:43 = %Y-%m-%d %H:%M:%S Formula to convert to POSIX time. Indicate with "TIMESTAMP" the source value to convert from. Example 1: For Siemens HMI ({TIMESTAMP}/1000000) - 25569) * 86400 * 1000 Example 2: For Excel Spreadsheet = ({TIMESTAMP} - 25569) * 86400 * 1000
Note on B33: Table Name: Required* Name of the SQL table. Example: LYOEvents *Only specify for datasources of type ODBC.
Note on B34: Filter Column: Required* *Only specify for datasources of type ODBC. Column that will determine the filter of the query to retrieve data from the Database. Indicate the name of the Inmation Column and map it in the Column Mapping table. Options: - ID: Filter by higher auto-incremental row index. - TimestampUTC or TimestampLocal: Fliter by higher timestamp. As recommendation, use ID when possible. When filtering by Timestamp data loss can occur. Any alarm/event entered into the database with a timestamp earlier than the current one may be lost. If the Timestamp format is in string format the SQL data must be sorted. If the timestamp format is in string format, the alphabetical order of it must coincide with the chronological order of the data. If this is not fulfilled, the ID must be used as the Filter Column.
Note on B37: Column Mapping: Required Table to change the field names provided by the source to more generic or comprehensive names. Enhances comprehension in the system:inmation. Optionally, a regular expression can be applied to obtain a partial part or a segment of the source value. The regular expression is applied to the value of the Source Column. Workflow: 1. Map Source Column into an Inmation Column. 2. Apply Regular Expression to source values.
Note on B38: Source Column: Required Field names provided from the source. Example 1: For ODBC datasources, indicate the column names: Datetime, State, Name. Example 2: For OPC UA and OPC AE datasources, indicate the address of the fields recieved by the datasource in Inmation: u_.2041.WinCCEventType.PRIORITY.d_, for a Priority field; u_.2041.2047.d_, for a TimestampLocal; Common.Message, for the Message of the event.
Note on C38: Inmation Column: Required Name of the alarm/event field in the system:inmation. At the end of the configuration, the mapped Inmation Columns must adhere to the following criteria: Required Inmation Columns: - MsgID - MsgState (only required for Type 'Alarms'), (one of)*: - CAME - GONE - CAME ACK - GONE ACK - MsgDescription - TimestampUTC or TimestampLocal (only one is required, mapping both is optional) - ID (only required for ODBCs with Filter Column 'ID') Optional Inmation Columns: - GMPCritical (if not defined, this column will default to "NO"), (one of)*: - YES - NO - SfoID - OrderID - BatchID - ProductionUnit - EquipmentID - OperationID - PhaseID - StepID - User - UserComment Automatically mapped Inmation Columns: These columns are automatically mapped by the ITL and cannot be mapped. - EquipmentISA95 - MsgType - DatasourcePath Additional Information Exceptions that will be sent to MES: The exception will be mapped with the following priority: 1. SfoID 2. OrderID 3. BatchID 4. ProductionUnit 5. EquipmentID (if not mapped, it will be obtained from the MES Name of the ISA 95 Level. If the MES Name is empty, it will be obtained from the name of the object in the ISA-95 Equipment Model of SAIL) Custom Inmation Columns: In addition to the required and optional Inmation Columns, the system supports the definition of as many custom columns as needed. Custom columns will be historized as well. *The value needs to fit the standardized values.
Note on D38: Regular Expression: Optional Transformation of the source data. Indicate the Lua pattern to extract the data desired. Typically used to extract specific characters from a source. Example 1: Extract the event ID from an event log entry. Source Data: "EventID: 4567 - Alarm triggered at zone 3" Regular Expression: "EventID: (%d+)" --> Matches the digits following "EventID: ", capturing the event ID number. Returns: "4567" Example 2: Extract the timestamp from an alarm log entry. Source Data: "Alarm at 2024-05-29 14:32:21 - Zone 5" Regular Expression: "(%d%d%d%d%-%d%d%-%d%d %d%d:%d%d:%d%d)" --> Matches the timestamp in the format "YYYY-MM-DD HH:MM". Returns: "2024-05-29 14:32:21" Example 3: Extract the alarm type from an alarm log entry. Source Data: "AlarmType: Fire - Location: Warehouse" Regular Expression: "AlarmType: (%a+)" --> Matches the word following "AlarmType: ", capturing the type of alarm. Returns: "Fire"
Note on B58: Format Mapping: Optional Table to format Inmation Columns resultant form the Column Mapping or to create new ones. - Use "{}" to encapsulate/indicate an Inmation Column. - All other characters will be treated as fixed values. Workflow: Update the value of an Inmation Column with the formatting specified in the Formatting column. If the Inmation Column does not exists, create an Inmation Column with the value specified in the Formatting column. Note: the format in the examples is <Formatting>; <Inmation Column>. Example 1: {MsgID} {Name}; MsgDescription --> Creates/Updates the Inmation Column "MsgDescription" with the concatenation of the two columns. If MsgID = 122 and Name = "RPM high", then the resultant column: MsgDescription = "122 RPM high". Example 2: LOW; Severity --> Creates/Updates the Inmation Column "Severity" with the values: Severity = "LOW". Example 3: alarmID: {MsgID}; id2 --> Creates/Updates the Inmation Column "id2" with the fixed value "alarmID: ". The resultant column (note: same MsgID as the Example1): id2 = "alarmID: 122". Example 4: {description1} - {description2}; description3 --> Creates/Updates the Inmation Column "description3". If description1= "RPM too high" and descrption2="Over 4000", then the resultant column: descripiton3="RPM too high - Over 4000".
Note on B59: Formatting: Required Formatting endured to create/update a new/existing Inmation Column. Encapsulate the names of Inmation Columns in between brackets "{...}". All other characters will be treated as fixed values. Example 1: Concatenation of two columns: {Descripiton}{Severity} Example 2: Adding a new column with the fixed value LOW: LOW Example 3: Combination of a fixed value with a source column: alarmID: {ID} Example 4: Combination of two source columns with a fixed value in between: {description1} - {description2}
Note on C59: Inmation Column: Required Name of the alarm/event field in the system:inmation. At the end of the configuration, the mapped Inmation Columns must adhere to the following criteria: Required Inmation Columns: - MsgID - MsgState (only required for Type 'Alarms'), (one of)*: - CAME - GONE - CAME ACK - GONE ACK - MsgDescription - TimestampUTC or TimestampLocal (only one is required, mapping both is optional) - ID (only required for ODBCs with Filter Column 'ID') Optional Inmation Columns: - GMPCritical (if not defined, this column will default to "NO"), (one of)*: - YES - NO - SfoID - OrderID - BatchID - ProductionUnit - EquipmentID - OperationID - PhaseID - StepID - User - UserComment Automatically mapped Inmation Columns: These columns are automatically mapped by the ITL and cannot be mapped. - EquipmentISA95 - MsgType - DatasourcePath Additional Information Exceptions that will be sent to MES: The exception will be mapped with the following priority: 1. SfoID 2. OrderID 3. BatchID 4. ProductionUnit 5. EquipmentID (if not mapped, it will be obtained from the MES Name of the ISA 95 Level. If the MES Name is empty, it will be obtained from the name of the object in the ISA-95 Equipment Model of SAIL) Custom Inmation Columns: In addition to the required and optional Inmation Columns, the system supports the definition of as many custom columns as needed. Custom columns will be historized as well. *The value needs to fit the standardized values.
Note on B65: Value Mapping: Optional Table to map the values given by the source to more comprehensive or meaningful values. Workflow: If the Source Value matches the value of the Inmation Column, then overwrite the Inmation Column with the value specified in the Inmation Value. - The Source Value can be defined as "{Default}", which will set a default Inmation Value in case no condition is matched. - To specify a null value, type "{nil}". Note: the format in the examples is <Inmation Column>; <Source Value>; <Inmation Value>. Example 1: StateID; 1; CAME --> if the source value of the inmation field StateID is 1 then overwrite StateID with the value CAME. Example 2: Severity; 0; HIGH --> if the source value of the inmation field Severity is 0 then overwrite Severity with the value GONE.
Note on B66: Inmation Column: Required Name of the alarm/event field in the system:inmation. At the end of the configuration, the mapped Inmation Columns must adhere to the following criteria: Required Inmation Columns: - MsgID - MsgState (only required for Type 'Alarms'), (one of)*: - CAME - GONE - CAME ACK - GONE ACK - MsgDescription - TimestampUTC or TimestampLocal (only one is required, mapping both is optional) - ID (only required for ODBCs with Filter Column 'ID') Optional Inmation Columns: - GMPCritical (if not defined, this column will default to "NO"), (one of)*: - YES - NO - SfoID - OrderID - BatchID - ProductionUnit - EquipmentID - OperationID - PhaseID - StepID - User - UserComment Automatically mapped Inmation Columns: These columns are automatically mapped by the ITL and cannot be mapped. - EquipmentISA95 - MsgType - DatasourcePath Additional Information Exceptions that will be sent to MES: The exception will be mapped with the following priority: 1. SfoID 2. OrderID 3. BatchID 4. ProductionUnit 5. EquipmentID (if not mapped, it will be obtained from the MES Name of the ISA 95 Level. If the MES Name is empty, it will be obtained from the name of the object in the ISA-95 Equipment Model of SAIL) Custom Inmation Columns: In addition to the required and optional Inmation Columns, the system supports the definition of as many custom columns as needed. Custom columns will be historized as well. *The value needs to fit the standardized values.
Note on C66: Source Value: Required Source value to be compared against. The Source Value can be defined as "{Default}", which will set a default Inmation Value in case no condition is matched. To specify a null value, type "{nil}". Example: 0, {Default}, {nil}
Note on D66: Inmation Value: Required Value of the field after the mapping. Example: CAME
Note on B73: Inmation Mapping: Optional Map the Inmation Column with the value of a tag in the system:inmation if a condition is met. - The value of the inmation tag will be obtained from the path of the object indicated in the Path column. - The condition is composed by the columns Inmation Condition Column, Operand and Inmation Value, and has the form: <Inmation Condition Column> <Operand> <Inmation Value>. Condition: - Indicate a default case leaving the 3 condition columns empty. - If a default case, the Inmation Column will always be populated with the value of the inmation tag. - If a condition is specified, the value will be mapped only if the condition is true. - If a condition is specified but not met and no default case is specified, the Inmation Column will not be mapped. - Cases with a matching condition always take precedence over default cases, overwriting them. - If two or more matching conditions are defined, only the latter takes precedence. Note: The format in the examples is <Inmation Column>; <Path>; <Inmation Condition Column>; <Operand>; <Inmation Value>. Example 1: SfoID; <path>; BatchID; EQ; Room01 --> if the value of the BatchID field matches "Room01", then populate the column SfoID with the value of the inmation tag. Example 2: SfoID; <path>; (empty); (empty); (empty) --> Populate a new column called SfoID with the value of the inmation tag.
Note on B74: Inmation Column: Required Name of the alarm/event field in the system:inmation. At the end of the configuration, the mapped Inmation Columns must adhere to the following criteria: Required Inmation Columns: - MsgID - MsgState (only required for Type 'Alarms'), (one of)*: - CAME - GONE - CAME ACK - GONE ACK - MsgDescription - TimestampUTC or TimestampLocal (only one is required, mapping both is optional) - ID (only required for ODBCs with Filter Column 'ID') Optional Inmation Columns: - GMPCritical (if not defined, this column will default to "NO"), (one of)*: - YES - NO - SfoID - OrderID - BatchID - ProductionUnit - EquipmentID - OperationID - PhaseID - StepID - User - UserComment Automatically mapped Inmation Columns: These columns are automatically mapped by the ITL and cannot be mapped. - EquipmentISA95 - MsgType - DatasourcePath Additional Information Exceptions that will be sent to MES: The exception will be mapped with the following priority: 1. SfoID 2. OrderID 3. BatchID 4. ProductionUnit 5. EquipmentID (if not mapped, it will be obtained from the MES Name of the ISA 95 Level. If the MES Name is empty, it will be obtained from the name of the object in the ISA-95 Equipment Model of SAIL) Custom Inmation Columns: In addition to the required and optional Inmation Columns, the system supports the definition of as many custom columns as needed. Custom columns will be historized as well. *The value needs to fit the standardized values.
Note on C74: Path: Required Path of the tag in the system:inmation. Specify relative path of the redundant items folder, starting from the Site level: /<Site>/<Area>/ ... Example: /ATLNZ/Line C/BufferPreparation/BagDistribution(CB90)/D101/CB90_D101_VE_batch_ID
Note on D74: Inmation Condition Column: Optional Specify the Inmation Column whose value will be compared against the Inmation Value. To specify a default condition, leave the field empty. Examples: Datetime, State, Name, (empty).
Note on E74: Operand: Optional Operand of the boolean expression. To specify a default condition, leave the field empty. Options: - LT : Less than - GT : Greater than - LTE : Less or equal than - GTE : Greater or equal than - EQ : Equal to - NE : Not equal to - (empty) : Indicates default condition
Note on F74: Inmation Value: Optional Value that will be used to create the condition. It will be compared against the Inmation Condition Column. To specify a default condition, leave the field empty. To specify a null value, type "{nil}". Example: Room01, (empty).
Note on B80: Filter: Optional Table that defines which alarms/events pass the filter (will be processed). Workflow: If more than one filter is specified for the same Inmation Column, then the filters are concatenated with an OR operator. The concatenation between different Inmation Columns is done by an AND operator. Note: the format in the examples is <Inmation Column >; <Operand>; <Condition Value> Example 1: MsgState; EQ; CAME MsgState; EQ; GONE --> process those alarms which state value is CAME or GONE. Example 2: Priority; EQ; CRITICAL Severity; EQ; HIGH --> process those alarms with a priority CRITICAL and, of those, the ones that have a severity equal to HIGH.
Note on B81: Inmation Column: Required Name of the alarm/event field in the system:inmation. At the end of the configuration, the mapped Inmation Columns must adhere to the following criteria: Required Inmation Columns: - MsgID - MsgState (only required for Type 'Alarms'), (one of)*: - CAME - GONE - CAME ACK - GONE ACK - MsgDescription - TimestampUTC or TimestampLocal (only one is required, mapping both is optional) - ID (only required for ODBCs with Filter Column 'ID') Optional Inmation Columns: - GMPCritical (if not defined, this column will default to "NO"), (one of)*: - YES - NO - SfoID - OrderID - BatchID - ProductionUnit - EquipmentID - OperationID - PhaseID - StepID - User - UserComment Automatically mapped Inmation Columns: These columns are automatically mapped by the ITL and cannot be mapped. - EquipmentISA95 - MsgType - DatasourcePath Additional Information Exceptions that will be sent to MES: The exception will be mapped with the following priority: 1. SfoID 2. OrderID 3. BatchID 4. ProductionUnit 5. EquipmentID (if not mapped, it will be obtained from the MES Name of the ISA 95 Level. If the MES Name is empty, it will be obtained from the name of the object in the ISA-95 Equipment Model of SAIL) Custom Inmation Columns: In addition to the required and optional Inmation Columns, the system supports the definition of as many custom columns as needed. Custom columns will be historized as well. *The value needs to fit the standardized values.
Note on C81: Operand: Required Operand of the boolean expression. Options: - LT : Less than - GT : Greater than - LTE : Less or equal than - GTE : Greater or equal than - EQ : Equal to - NE : Not equal to
Note on D81: Condition Value: Required Value that will be processed in the boolean expression. Options: - Any string value : String value - Any numeric value : Numeric value - TRUE, FALSE : Boolean - {nil} : Null Examples: Alarm01, 100, CRITICAL, TRUE, {nil}
Note on B97: Alarms/Events List: Optional* This table indicates the list of relevant alarms/events. If Only List is set to 'YES', only the Alarms/Events specified here will be processed. - The column MsgID matches the MsgID of the Inmation Column defined in the configuration. - The column GMPCritical overwrites the resultant GMPCritical obtained. - The Comment column will be ignored when processing the Alarm/Event. Use it to provide a comment of the row. Workflow: The alarms/events specified here will be processed. The GMPCritical field of the Alarm/Event indicated by the MsgID will be updated. *If Only List is set to 'YES', this table is required.
Note on B98: MsgID: Required MsgID of the alarm/event Examples: 001, AL24-32
Note on C98: GMPCritical: Required Indicates if the alarm is GMPCritical or not. The GMPCritical indicated here overwrites the GMPCritical resultant of the configuration. Options: - YES - NO
Note on D98: Comment: Ignored Use to provide additional comments/information for the configuration of this alarm/event. This column will not be processed as an Inmation Column.

## SiemensRefComeGone
Meldezustände / Quittierzustände - SIMATIC Prozessleitsystem PCS 7 OpenPCS 7 (V9.1 … - ID: 109805405 - Industry Support Siemens
Meldezustand | EnabledState/Id | ActiveState/Id | AckedState/Id
Gesperrte Meldung | false | - | -
Freigegebene Meldung | true
Gekommene Meldung | true | true | false | true true false | 0 | Come
Gegangene Meldung mit Quittierung | true | false | true | true false true | 1 | Gone Ack
Gegangene Meldung ohne Quittierung | true | false | false | true false false | 2 | GONE
Quittierte Meldungen (Meldung steht noch an) | true | true | true | true true true | 3 | Come Ack
Quittierte Meldungen (Meldung steht nicht mehr an) | true | false | true | true false true | 1
Gekommene, quittierte Meldung | true | true | true | true true true | 3
Gekommene, gegangene Meldung mit Quittierung | true | false | true | true false true | 1
Gekommene, gegangene Meldung ohne Quittierung | true | false | false | true false false | 2
Vom System quittierte Meldung | true | true | true | true true true | 3
(Meldung steht noch an)
Vom System quittierte Meldung (Meldung steht nicht mehr an) | true | false | true | true false true | 1
Notquittierte Meldung (Meldung steht noch an) | true | true | true | true true true | 3
Notquittierte Meldung (Meldung steht nicht mehr an) | true | false | true | true false true | 1

## SiemensMeldearten
ALG_Type | Meldearten | Meldeart
[TYPE_NAME_TEXTID][66036][1] | [TYPE_NAME_L1031][67568116][7] | [TYPE_NAME_L1033][67699188][7] | [TYPE_NAME_L1034][67764724][7] | [TYPE_NAME_L1036][67895796][7] | [TYPE_NAME_L1040][68157940][7] | [TYPE_ID][527][1] | [TYPE_CLASS][529][1] | [TYPE_QUIT_COME][501][2] | [TYPE_QUIT_GO][502][2] | [TYPE_QUIT_FLASH][503][2] | [TYPE_QUIT_FIRSTFLASH][504][2] | [TYPE_QUIT_NOGO][505][2] | [TYPE_QUIT_UNIQUE_USER][506][2] | [TYPE_QUIT_ONL_COM_COME][507][2] | [TYPE_QUIT_COMMENT][530][2] | [TYPE_QUIT_SIGNATURE][531][2] | [TYPE_HUPE_QUIT][508][2] | [TYPE_HUPE_VAR][509][1] | [TYPE_COME_TEXTID][66046][1] | [TYPE_COME_L1031][67568126][7] | [TYPE_COME_L1033][67699198][7] | [TYPE_COME_L1034][67764734][7] | [TYPE_COME_L1036][67895806][7] | [TYPE_COME_L1040][68157950][7] | [TYPE_GONE_TEXTID][66047][1] | [TYPE_GONE_L1031][67568127][7] | [TYPE_GONE_L1033][67699199][7] | [TYPE_GONE_L1034][67764735][7] | [TYPE_GONE_L1036][67895807][7] | [TYPE_GONE_L1040][68157951][7] | [TYPE_QUIT_TEXTID][66048][1] | [TYPE_QUIT_L1031][67568128][7] | [TYPE_QUIT_L1033][67699200][7] | [TYPE_QUIT_L1034][67764736][7] | [TYPE_QUIT_L1036][67895808][7] | [TYPE_QUIT_L1040][68157952][7] | [TYPE_CG_TEXTID][66049][1] | [TYPE_CG_L1031][67568129][7] | [TYPE_CG_L1033][67699201][7] | [TYPE_CG_L1034][67764737][7] | [TYPE_CG_L1036][67895809][7] | [TYPE_CG_L1040][68157953][7] | [TYPE_TAG_STATE][514][1] | [TYPE_TAG_STATEBIT][515][1] | [TYPE_TAG_LOCK][516][1] | [TYPE_TAG_LOCKBIT][517][1] | [TYPE_TAG_QUIT][518][1] | [TYPE_TAG_QUITBIT][519][1] | [TYPE_COME_TEXTCO][521][12] | [TYPE_COME_BKCO][522][12] | [TYPE_GO_TEXTCO][523][12] | [TYPE_GO_BKCO][524][12] | [TYPE_QUIT_TEXTCO][525][12] | [TYPE_QUIT_BKCO][526][12] | [TYPE_CREATORID][528][1]
Name (ID) | Name (DEU) | Name (ENU) | Name (ESP) | Name (FRA) | Name (ITA) | Meldeart (ID) | Meldeklasse | Quittierung "gekommen" | Quittierung "gegangen" | Blinken ein | Nur bei Erstwert | Ohne Zustand "gegangen" | Eindeutiger Benutzer | Kommentar "gekommen" | Kommentar erforderlich | Signatur erforderlich | Quittiertaste | Variable für zentralen Melder | "gekommen" (ID) | "gekommen" (DEU) | "gekommen" (ENU) | "gekommen" (ESP) | "gekommen" (FRA) | "gekommen" (ITA) | "gegangen" (ID) | "gegangen" (DEU) | "gegangen" (ENU) | "gegangen" (ESP) | "gegangen" (FRA) | "gegangen" (ITA) | "quittiert" (ID) | "quittiert" (DEU) | "quittiert" (ENU) | "quittiert" (ESP) | "quittiert" (FRA) | "quittiert" (ITA) | "gekommen und gegangen" (ID) | "gekommen und gegangen" (DEU) | "gekommen und gegangen" (ENU) | "gekommen und gegangen" (ESP) | "gekommen und gegangen" (FRA) | "gekommen und gegangen" (ITA) | Zustandsvariable | Zustandsbit | Sperrvariable | Sperrbit | Quittiervariable | Quittierbit | Schriftfarbe "gekommen" | Hintergrundfarbe "gekommen" | Schriftfarbe "gegangen" | Hintergrundfarbe "gegangen" | Schriftfarbe "quittiert" | Hintergrundfarbe "quittiert" | Autor
97 | Alarm - oben | Alarm High | Alarma superior | Alarme supérieure | Allarme superiore | 1 | Alarm | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 255; 255; 255 | 255; 0; 0 | 255; 255; 255 | 255; 0; 0 | 255; 255; 255 | 255; 0; 0 | 0
98 | Alarm - unten | Alarm Low | Alarma inferior | Alarme inférieure | Allarme inferiore | 2 | Alarm | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 255; 255; 255 | 255; 0; 0 | 255; 255; 255 | 255; 0; 0 | 255; 255; 255 | 255; 0; 0 | 0
99 | Warnung - oben | Warning High | Advertencia superior | Avertissement supérieur | Avviso superiore | 19 | Warnung | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 0; 0; 0 | 255; 255; 0 | 0; 0; 0 | 255; 255; 0 | 0; 0; 0 | 255; 255; 0 | 0
100 | Warnung - unten | Warning Low | Advertencia inferior | Avertissement inférieur | Avviso inferiore | 20 | Warnung | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 0; 0; 0 | 255; 255; 0 | 0; 0; 0 | 255; 255; 0 | 0; 0; 0 | 255; 255; 0 | 0
101 | Toleranz - oben | Tolerance High | Tolerancia superior | Tolérance supérieure | Tolleranza superiore | 37 | Toleranz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 255; 255; 255 | 0; 0; 255 | 255; 255; 255 | 0; 0; 255 | 255; 255; 255 | 0; 0; 255 | 0
102 | Toleranz - unten | Tolerance Low | Tolerancia inferior | Tolérance inférieure | Tolleranza inferiore | 38 | Toleranz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 255; 255; 255 | 0; 0; 255 | 255; 255; 255 | 0; 0; 255 | 255; 255; 255 | 0; 0; 255 | 0
1 | Störung | Failure | Avería | Défaut | Guasto | 55 | AS Leittechnik-Meldungen | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 255; 255; 0 | 0; 0; 0 | 255; 255; 0 | 0; 0; 0 | 255; 255; 0 | 0; 0; 0 | 0
10 | Fehler | Error | Error | Erreur | Errore | 56 | AS Leittechnik-Meldungen | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 255; 255; 0 | 0; 0; 0 | 255; 255; 0 | 0; 0; 0 | 255; 255; 0 | 0; 0; 0 | 0
1 | Störung | Failure | Avería | Défaut | Guasto | 71 | OS Leittechnik-Meldungen | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 255; 255; 0 | 0; 0; 0 | 255; 255; 0 | 0; 0; 0 | 255; 255; 0 | 0; 0; 0 | 0
10 | Fehler | Error | Error | Erreur | Errore | 72 | OS Leittechnik-Meldungen | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 255; 255; 0 | 0; 0; 0 | 255; 255; 0 | 0; 0; 0 | 255; 255; 0 | 0; 0; 0 | 0
103 | Wartung | Maintenance | Mantenimiento | Maintenance | Manutenzione | 89 | Vorbeugende Wartung | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 255; 255; 0 | 0; 0; 0 | 255; 255; 0 | 0; 0; 0 | 255; 255; 0 | 0; 0; 0 | 0
104 | Prozessmeldung | Process message | Aviso de proceso | Alarme de process | Segnalazione di processo | 106 | Prozessmeldung Klasse | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 255; 255; 255 | 0; 128; 128 | 255; 255; 255 | 0; 128; 128 | 255; 255; 255 | 0; 128; 128 | 0
104 | Prozessmeldung | Process message | Aviso de proceso | Alarme de process | Segnalazione di processo | 122 | Betriebsmeldung Klasse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 255; 255; 255 | 0; 128; 128 | 255; 255; 255 | 0; 128; 128 | 255; 255; 255 | 0; 128; 128 | 0
105 | Bedienanforderung | Request for Operator Input | Solicitud de intervención | Demande d'intervention | Richiesta dell'operatore | 139 | Bedienanforderung Klasse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 255; 255; 255 | 128; 0; 128 | 255; 255; 255 | 128; 0; 128 | 255; 255; 255 | 128; 0; 128 | 0
106 | Bedienmeldung | Operator Message | Aviso de operador | Message de conduite | Segnalazione dell'operatore | 156 | Bedienmeldung Klasse | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 255; 255; 255 | 128; 0; 128 | 255; 255; 255 | 128; 0; 128 | 255; 255; 255 | 128; 0; 128 | 0
107 | Status AS | Status PLC | Estado AS | Etat API | Stato AS | 253 | Status-Meldung | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 255; 255; 255 | 0; 128; 128 | 255; 255; 255 | 0; 128; 128 | 255; 255; 255 | 0; 128; 128 | 0
108 | Status OS | Status OS | Estado OS | Etat OS | Stato OS | 254 | Status-Meldung | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 255; 255; 255 | 0; 128; 128 | 255; 255; 255 | 0; 128; 128 | 255; 255; 255 | 0; 128; 128 | 0
11 | Leittechnik | Process control system | Sistema de control de procesos | Contrôle de processus | Sistema di controllo di processo | 257 | System, quittierpflichtig | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 0; 0; 0 | 192; 192; 192 | 0; 0; 0 | 192; 192; 192 | 0; 0; 0 | 192; 192; 192 | 0
12 | Systemmeldungen | System messages | Avisos de sistema | Alarmes système | Segnalazione di sistema | 258 | System, quittierpflichtig | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 0; 0; 0 | 192; 192; 192 | 0; 0; 0 | 192; 192; 192 | 0; 0; 0 | 192; 192; 192 | 0
11 | Leittechnik | Process control system | Sistema de control de procesos | Contrôle de processus | Sistema di controllo di processo | 273 | System, nicht quittierpflichtig | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 0; 0; 0 | 192; 192; 192 | 0; 0; 0 | 192; 192; 192 | 0; 0; 0 | 192; 192; 192 | 0
13 | Bedienmeldungen | Operator input messages | Avisos de operador | Alarmes de conduite | Segnalazioni di operativa | 274 | System, nicht quittierpflichtig | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 83 | K | C | A | A | E | 84 | G | G | D | P | U | 86 | QS | QS | AG | QS | RC | 85 | KG | CG | AD | AP | EU |  | 0 |  | 0 |  | 0 | 0; 0; 0 | 192; 192; 192 | 0; 0; 0 | 192; 192; 192 | 0; 0; 0 | 192; 192; 192 | 0
81 | Benachrichtigung | Notification | Notificación | Notification | Notifica | 275 | System, nicht quittierpflichtig | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | + | + | + | + | + | 3 | - | - | - | - | - | 5 | * | * | * | * | * | 4 | +/- | +/- | +/- | +/- | +/- |  | 0 |  | 0 |  | 0 | 0; 0; 0 | 192; 192; 192 | 0; 0; 0 | 192; 192; 192 | 0; 0; 0 | 192; 192; 192 | 0

## SiemensMeldeklasse
ALG_Class | Meldeklassen | Meldeklasse
[CLASS_NAME_TEXTID][65936][1] | [CLASS_NAME_L1031][67568016][7] | [CLASS_NAME_L1033][67699088][7] | [CLASS_NAME_L1034][67764624][7] | [CLASS_NAME_L1036][67895696][7] | [CLASS_NAME_L1040][68157840][7] | [CLASS_ID][421][1] | [CLASS_TAG_STATE][414][1] | [CLASS_TAG_STATEBIT][415][1] | [CLASS_TAG_LOCK][416][1] | [CLASS_TAG_LOCKBIT][417][1] | [CLASS_TAG_QUIT][418][1] | [CLASS_TAG_QUITBIT][419][1] | [CLASS_CREATORID][422][1]
Name (ID) | Name (DEU) | Name (ENU) | Name (ESP) | Name (FRA) | Name (ITA) | Klasse (ID) | Zustandsvariable | Zustandsbit | Sperrvariable | Sperrbit | Quittiervariable | Quittierbit | Autor
8 | Alarm | Alarm | Alarma | Alarme | Allarme | 1 |  | 0 |  | 0 |  | 0 | 10210
9 | Warnung | Warning | Advertencia | Avertissement | Avviso | 2 |  | 0 |  | 0 |  | 0 | 10210
87 | Toleranz | Tolerance | Tolerancia | Tolérance | Tolleranza | 3 |  | 0 |  | 0 |  | 0 | 10210
88 | AS Leittechnik-Meldungen | PLC process control messages | Avisos de control de procesos AS | Messages de contrôle de process AS | Segnalazioni del sistema di controllo di processo AS | 4 |  | 0 |  | 0 |  | 0 | 10210
89 | OS Leittechnik-Meldungen | OS process control system messages | Avisos de control de procesos OS | Messages de contrôle de process OS | Segnalazioni del sistema di controllo di processo OS | 5 |  | 0 |  | 0 |  | 0 | 10210
90 | Vorbeugende Wartung | Preventive maintenance | Mantenimiento preventivo | Maintenance préventive | Manutenzione preventiva | 6 |  | 0 |  | 0 |  | 0 | 10210
91 | Prozessmeldung Klasse | Process message class | Categoría de aviso de proceso | Alarme de processus - Classe | Classe segnalazione di processo | 7 |  | 0 |  | 0 |  | 0 | 10210
92 | Betriebsmeldung Klasse | Operational message class | Categoría de aviso de funcionamiento | Alarme de fonctionnement - Classe | Classe della segnalazione di servizio | 8 |  | 0 |  | 0 |  | 0 | 10210
93 | Bedienanforderung Klasse | Operator request class | Categoría de solicitud de intervención | Requête d'intervention - Classe | Classe della richiesta operativa | 9 |  | 0 |  | 0 |  | 0 | 10210
94 | Bedienmeldung Klasse | Operator message class | Categoría de aviso de operador | Alarme de conduite : classe | Classe della segnalazione dell'operatore | 10 |  | 0 |  | 0 |  | 0 | 10210
95 | Status-Meldung | Status Message | Aviso de estado | Message d'état | Segnalazione di stato | 16 |  | 0 |  | 0 |  | 0 | 10210
6 | System, quittierpflichtig | System, requires acknowledgment | Sistema, de acuse obligatorio | Système, acquittement requis | Sistema, con obbligo di riconoscimento | 17 |  | 0 |  | 0 |  | 0 | 10210
96 | System, nicht quittierpflichtig | System, does not require acknowledgment | Sistema, de acuse no obligatorio | Système, acquittement non requis | Sistema, senza obbligo di riconoscimento | 18 |  | 0 |  | 0 |  | 0 | 10210